## Slide 1
Modeling ASHP in REopt
Case Studies
June 24, 2024
DRAFT – NOT FOR CITATION, QUOTATION, OR DISTRIBUTION

## Slide 2
What financial impacts could thermal electrification via electric heater or air-source heat pump (ASHP) systems have on the studied site?
What are the most cost-effective size of ASHPs to serve space heating/cooling load and domestic hot water at the studied site?
What are the required size of ASHPs to replace existing heating/cooling systems to serve space heating/cooling load and domestic hot water at the studied site?
What are the emissions impacts of replacing the system’s existing boiler with these ASHP systems?
Key Questions Addressed by These Case Studies
DRAFT – NOT FOR CITATION, QUOTATION, OR DISTRIBUTION

## Slide 3: Case Studies Summary
ASHP Sizes + Performance
Energy Cost Savings
Emission Impacts
In cities in different climates
Cold Climate: Minneapolis, MN
Swing Climate: Chicago, IL
Hot Climate: Miami, FL
Other Climate: Los Angeles, CA
Different building types
Retail Store
Large Hotel
Secondary School
Midrise Apartment
Large Office
Six ASHP system configurations

## Slide 4
Fuel Cost Assumptions
DRAFT – NOT FOR CITATION, QUOTATION, OR DISTRIBUTION
City | Heating Gas [$/MMBtu] | Source
Minneapolis, MN | $10.2 | https://www.bls.gov/regions/midwest/data/averageenergyprices_selectedareas_table.htm
Chicago, IL | $10.0 | 
Miami, FL | $30.2 | 
Los Angeles, CA | $15.6 | 

## Slide 5
Discuss the 6 configs here
ASHP System Configurations in REopt
DRAFT – NOT FOR CITATION, QUOTATION, OR DISTRIBUTION

## Slide 6
Cold Climate City Case Study
Results for Minneapolis, MN

## Slide 7: System Configuration 1
Building Type | ASHP-SH size [ton] | ASHP-WH size [ton] | LCC [$] | NPV [$] | LCCC [$] | ASHP-SH Prod [mmbtu] | ASHP-WH Prod [mmbtu] | Existing Boiler Prod [mmbtu] | Existing Chiller Prod [ton] | Electric Heater Prod [mmbtu] | CO2 Emission Saving [ton] | Avoided Health Damages [$]
Large Office | 0 | 1.1 | 9.12M | 0.96k | 2.44k | 0 | 0 | 8.29k | 634k | 0 | 103 | 1,643
Large Hotel | 2.1 | 34 | 4.79M | 48.3k | 81.14k | 148 | 148 | 8.26k | 594k | 0 | 3,983 | 61,583
Midrise Apartment | 0 | 1.8 | 0.57M | 1.79k | 3.96k | 0 | 0 | 1.59k | 28k | 0 | 173 | 2,863
Retail Store | 0 | 0 | 0.87M | 0k | 0k | 0 | 0 | 1.50k | 36k | 0 | 0 | 0
Secondary School | 0 | 1.5 | 4.60M | 0.48k | 3.36 | 0 | 0 | 9.88k | 350k | 0 | 116 | 1,873
ASHP space heater and ASHP water heater can be deployed with existing boiler
Cooling load is supplied by existing chiller (ASHP does not provide cooling)
The cost-optimal solution deploys no or very small sized ASHP Space Heater
Most of heating load is provided by existing boiler

## Slide 8: System Configuration 1
Large Office
Large Hotel
Midrise Apartment
Retail Store
Secondary School
Space Heating
Space Cooling
DHW

## Slide 9: System Configuration 2
Building Type | ASHP-SH size [ton] | ASHP-WH size [ton] | LCC [$] | NPV [$] | LCCC [$] | ASHP-SH Prod [mmbtu] | ASHP-WH Prod [mmbtu] | Existing Boiler Prod [mmbtu] | Existing Chiller Prod [ton] | Electric Heater Prod [mmbtu] | CO2 Emission Saving [ton] | Avoided Health Damages [$]
Large Office | 0 |  |  |  |  |  |  |  |  |  |  | 
Large Hotel | 2.1 |  |  |  |  |  |  |  |  |  |  | 
Midrise Apartment | 0 |  |  |  |  |  |  |  |  |  |  | 
Retail Store | 0 |  |  |  |  |  |  |  |  |  |  | 
Secondary School | 0 |  |  |  |  |  |  |  |  |  |  | 
The cost-optimal solution deploys no or very small sized ASHP Space Heater
Most of heating load is provided by existing boiler
ASHP space heater and ASHP water heater forced to be deployed with resistive backup
Cooling load is supplied by existing chiller (ASHP does not provide cooling)

## Slide 10: System Configuration 2
Large Office
Large Hotel
Midrise Apartment
Retail Store
Secondary School
Space Heating
Space Cooling
DHW

## Slide 11: System Configuration 3
Building Type | ASHP-SH size [ton] | ASHP-WH size [ton] | LCC [$] | NPV [$] | LCCC [$] | ASHP-SH Prod [mmbtu/ton] | ASHP-WH Prod [mmbtu] | Existing Boiler Prod [mmbtu] | Existing Chiller Prod [kton] | Electric Heater Prod [mmbtu] | CO2 Emission Saving [ton] | Avoided Health Damages [$]
Large Office | 31.0 | 1.1 | 9.12M | 6.48k | 72.11k | 0.7k/ 66k | 699 | 7.6k | 568 | 0 | 1,151 | 42,134
Large Hotel | 79.4 | 34.0 | 4.84M | 235.1k | 255.2k | 1.7k/ 367k | 1,717 | 6.7k | 229 | 0 | 6,997 | 273,089
Midrise Apartment | 3.5 | 1.8 | 0.57M | 4.41k | 11.77k | 0.1k/ 6.9k | 135 | 1.5k | 21 | 0 | 371 | 7,975
Retail Store | 0 | 0 | 0.87M | 0 | 0 | 0 | 0 | 1.5k | 36 | 0 | 0 | 0
Secondary School | 0.3 | 1.5 | 4.60M | 0.5k | 4.0k | 6.4/ 484 | 6.4 | 9.9k | 349 | 0 | 125 | 2,186
When ASHP is used for both heating and cooling, it is mostly used for cooling
ASHP space heater can be deployed to serve both heating and cooling load
DHW load can be supplied by both ASHP water heater and existing boiler

## Slide 12: System Configuration 3
Large Office
Large Hotel
Midrise Apartment
Retail Store
Secondary School
Space Heating
Space Cooling
DHW

## Slide 13: System Configuration 4
Building Type | ASHP-SH size [ton] | ASHP-WH size [ton] | LCC [$] | NPV [$] | LCCC [$] | ASHP-SH Prod [mmbtu] | ASHP-WH Prod [mmbtu] | Existing Boiler Prod [mmbtu] | Existing Chiller Prod [ton] | Electric Heater Prod [mmbtu] | CO2 Emission Saving [ton] | Avoided Health Damages [$]
The cost-optimal solution deploys no or very small sized ASHP Space Heater
Most of heating load is provided by existing boiler
ASHP space heater is forced to be deployed to serve both heating and cooling load with resistive backup for heating
DHW load can be supplied by ASHP water heater only

## Slide 14: System Configuration 4
Large Office
Large Hotel
Midrise Apartment
Retail Store
Secondary School
Space Heating
Space Cooling
DHW

## Slide 15
Key Takeaways

## Slide 16
Appendix: REopt Model & Additional Modeling Assumptions

## Slide 17: REopt Energy Planning Platform
Formulated as a mixed integer linear program, REopt provides an integrated, cost-optimal energy solution.
Technology Options
Resources
Renewable Generation
Solar PV
Wind
Conventional Supply
Electric Grid & Fuel Supply
Conventional Generators
Combined Heat and Power
Energy Storage
Batteries
Thermal storage
Geothermal Heat Pumps
Drivers
Goals Minimize Cost
Clean Energy
Resilience
Economics
Technology Costs
Incentives
Financial Parameters
Energy Costs & Revenue
Energy & Demand Charges
Market Participation
Escalation Rates
Electric Loads
Thermal Loads
Energy Planning Platform
Techno-Economic Optimization
Optimized Minimum
Cost Solution
Technologies
Technology Mix
Technology Size
Operations
Optimal Dispatch
Project Economics
Capital Costs
Operating Costs
Net Present Value
Progress Toward Goals
Emissions Reduction
Length of Outage Sustained
DRAFT – NOT FOR CITATION, QUOTATION, OR DISTRIBUTION

## Slide 18
REopt Minimizes the System’s Lifecycle Cost of Energy
DRAFT – NOT FOR CITATION, QUOTATION, OR DISTRIBUTION
Economic Incentives (if Available)
Cost of Purchasing Electricity from Utility
Operational Costs
LCC of Energy System
Capital Cost of New Investment
Life cycle cost (LCC) of energy: The present value of all energy costs at the studied site throughout the analysis period (25 years).
Net present value (NPV): The lifecycle cost savings (difference in LCC) between the business-as-usual (BAU) case and the investment case.
  If NPV > 0, the new system yields savings to BAU
  If NPV < 0, the new system is more expensive than BAU
LCC of New Energy System
LCC of BAU
NPV

## Slide 19: How Can You Use REopt?
Easy-to-use, free web tool
reopt.nrel.gov
https://github.com/nrel/reopt-api-analysis/wiki
https://github.com/NREL/REopt_API and https://github.com/NREL/REopt.jl
Custom NREL analysis
Open-source codebase
Application Programming Interface (API)